## EXHIBIT A
[6 empty] | Column A | Column B | Column C | Column D | Column E
Item |  | Description |  |  |  | Quantity Each (A) | New Unit Price (B) | Subtotal (A * B) | Recertified Unit Price ( C) | Subtotal (A * C)
1 | 200 CLASS CFH (NTC) SCREWED CASE ALUMINUM GAS METERS WITH CONNECTIONS (General) |  |  |  |  | 2400 |  | 0 |  | 0
1) HUBS: SPRAGUE 1A
2) CAPACITY: 250 CFH OF .60 SG NATURAL GAS AT 1/2" W.C. DIFFERENTIAL
3) MAXIMUM WORKING PRESSURE: 5 PSIG
4) CONNECTIONS: 2 - INSUL 3/4" MALE PIPE THREAD GALV.
5) COMPATIBLE WITH ERT MODEL ERG-5006
2 | 200 CLASS CFH (NTC) SCREWED CASE ALUMINUM GAS METERS WITH CONNECTIONS (ITRON for use with 005 endpoint) |  |  |  |  | 400 |  | 0 |  | 0
1) HUBS: SPRAGUE 1A
2) CAPACITY: 250 CFH OF .60 SG NATURAL GAS AT 1/2" W.C. DIFFERENTIAL
3) MAXIMUM WORKING PRESSURE: 5 PSIG
4) CONNECTIONS: 2 - INSUL 3/4" MALE PIPE THREAD GALV.
5) COMPATIBLE WITH ERT MODEL ERG-5006-005
3 | 400 CLASS CFH (NTC) ALUMINUM GAS METERS WITH CONNECTIONS |  |  |  |  | 500 |  | 0 |  | 0
1) HUBS: AMERICAN 425 - 45 LT.; INVENSYS 415 - 45 LT.: ACTARIS 400 - SPRAGUE STD.
2) CAPACITY: 400 CFH OF .60 SG NATURAL GAS AT 1/2" W.C. DIFFERENTIAL
3) MAXIMUM WORKING PRESSURE: 10 PSIG
4) CONNECTIONS: 2 - 1 1/2" INSULATED MALE SWIVELS
5) COMPATIBLE WITH ERT MODEL ERG-5006
4 | 600 CLASS CFH (NTC) ALUMINUM GAS METERS WITH CONNECTIONS |  |  |  |  | 500 |  | 0 |  | 0
1) HUBS: 45 LT.
2) CAPACITY: 630 CFH OF .60 SG NATURAL GAS AT 1/2" W.C. DIFFERENTIAL
3) MAXIMUM WORKING PRESSURE: 25 PSIG
4) CONNECTIONS: 2 - 1 1/2" INSULATED MALE SWIVELS
5) COMPATIBLE WITH ERT MODEL ERG-5006
5 | 600 CLASS CFH (NTC) ALUMINUM GAS METERS WITH CONNECTIONS (Can be used for right to left) |  |  |  |  | 25 |  | 0 |  | 0
1) HUBS: 45 LT.
2) CAPACITY: 630 CFH OF .60 SG NATURAL GAS AT 1/2" W.C. DIFFERENTIAL
3) MAXIMUM WORKING PRESSURE: 25 PSIG
4) CONNECTIONS: 2 - 1 1/2" INSULATED MALE SWIVELS
5) COMPATIBLE WITH ERT MODEL ERG-5006
6 | 800 CLASS CFH (NTC) ALUMINUM GAS METERS WITH CONNECTIONS |  |  |  |  | 100 |  | 0 |  | 0
1) HUBS: SPRAGUE STANDARD
2) CAPACITY: 1000 CFH OF .60 SG NATURAL GAS AT 1/2" W.C. DIFFERENTIAL
3) MAXIMUM WORKING PRESSURE: 25 PSIG
4) CONNECTIONS 2 - 2" FEMALE INSULATED FEMALE SWIVEL GALVANIZED
5) COMPATIBLE WITH ERT MODEL ERG-5006
7 | 800 CLASS CFH (NTC) ALUMINUM GAS METERS WITH CONNECTIONS (With 2lb dial) |  |  |  |  | 100 |  | 0 |  | 0
1) HUBS: SPRAGUE STANDARD
2) CAPACITY: 1000 CFH OF .60 SG NATURAL GAS AT 1/2" W.C. DIFFERENTIAL
3) MAXIMUM WORKING PRESSURE: 25 PSIG
4) CONNECTIONS 2 - 2" FEMALE INSULATED FEMALE SWIVEL GALVANIZED
5) COMPATIBLE WITH ERT MODEL ERG-5006
8 | 1000 CLASS CFH (NTC) ALUMINUM GAS METERS WITH CONNECTIONS (With 2 lb Dial) |  |  |  |  | 200 |  | 0 |  | 0
1) HUBS: SPRAGUE STANDARD
2) CAPACITY: 1000 CFH OF .60 SG NATURAL GAS AT 1/2" W.C. DIFFERENTIAL
3) MAXIMUM WORKING PRESSURE: 25 PSIG
4) CONNECTIONS 2 - 2" FEMALE INSULATED FEMALE SWIVEL GALVANIZED
5) COMPATIBLE WITH ERT MODEL ERG-5006
9 | 1000 CLASS CFH (NTC) ALUMINUM GAS METERS WITH CONNECTIONS (With 2 lb Dial) Right to left |  |  |  |  | 20 |  | 0 |  | 0
1) HUBS: SPRAGUE STANDARD
2) CAPACITY: 1000 CFH OF .60 SG NATURAL GAS AT 1/2" W.C. DIFFERENTIAL
3) MAXIMUM WORKING PRESSURE: 25 PSIG
4) CONNECTIONS 2 - 2" FEMALE INSULATED FEMALE SWIVEL GALVANIZED
5) COMPATIBLE WITH ERT MODEL ERG-5006
10 | 1000 CLASS CFH (NTC) ALUMINUM GAS METERS WITH CONNECTIONS (With 7 inch Dial) |  |  |  |  | 200 |  | 0 |  | 0
1) HUBS: SPRAGUE STANDARD
2) CAPACITY: 1000 CFH OF .60 SG NATURAL GAS AT 1/2" W.C. DIFFERENTIAL
3) MAXIMUM WORKING PRESSURE: 25 PSIG
4) CONNECTIONS 2 - 2" FEMALE INSULATED FEMALE SWIVEL GALVANIZED
5) COMPATIBLE WITH ERT MODEL ERG-5006
11 | 1000 CLASS CFH (NTC) ALUMINUM GAS METERS WITH CONNECTIONS (With 7 inch Dial) Right to Left |  |  |  |  | 20 |  | 0 |  | 0
1) HUBS: SPRAGUE STANDARD
2) CAPACITY: 1000 CFH OF .60 SG NATURAL GAS AT 1/2" W.C. DIFFERENTIAL
3) MAXIMUM WORKING PRESSURE: 25 PSIG
4) CONNECTIONS 2 - 2" FEMALE INSULATED FEMALE SWIVEL GALVANIZED
5) COMPATIBLE WITH ERT MODEL ERG-5006
[6 empty] | Column A | Column B | Column C | Column D | Column E
Item |  | Description |  |  |  | Quantity Each (A) | New Unit Price (B) | Subtotal (A * B) | Recertified Unit Price ( C) | Subtotal (A * C)
12 | ROMET OR ROOTS 3M ROTARY METER OR EQUIVALENT |  |  |  |  | 30 |  | 0 |  | 0
| 1) Base Rate (Q.Max) : |  |  | 3000 acfh
| 2) Rangeability (+/-1%): |  |  | 76:1 ratio
| 3) Rangeability (+/- 2%): |  |  | 139:1 ratio
| 4) Start Rate: |  |  | 2.1 cfh
| 5) Stop Rate |  |  | 1.8 cfh
| 6) Flow Rate @ 0.5" W.C. Gas: |  |  | 2580 cfh
| 7) Avg. Differential, 100% Flow: |  |  | 1.05 in w.c.
| 8) Max. Operating Speed: |  |  | 2000 rpm
| 9) Gear Ratio: |  |  | 400:1 ratio
| 10) Displaced Volume/ Revolution: |  |  | 0.025 cf
| 11) Drive Rate, CD: |  |  | 10 cf/rev
| 12) Drive Rate, TD: |  |  | 100 cf/rev
| 13) Odometer Turnover: |  |  | 3.8 yrs.
| 14) Nominal Pipe Size: |  |  | 2 in.
| 15) Flange-to-Flange: |  |  | 6-3/4 in.
| 16) Bolts per Flange: |  |  | 4
| 17) Flange Bolt Hole Depth |  |  | 15/16 in.
| 18) Restricting Orfice (120%): |  |  | 17/32 in.
13 | ROMET OR ROOTS 5M ROTARY METER OR EQUIVALENT |  |  |  |  | 30 |  | 0 |  | 0
| 1) Base Rate (Q.Max) : |  |  | 5000 acfh
| 2) Rangeability (+/-1%): |  |  | 120:1 ratio
| 3) Rangeability (+/- 2%): |  |  | 215:1 ratio
| 4) Start Rate: |  |  | 1.2 cfh
| 5) Stop Rate |  |  | 0.8 cfh
| 6) Flow Rate @ 0.5" W.C. Gas: |  |  | 3975 cfh
| 7) Avg. Differential, 100% Flow: |  |  | 1.05 in. w.c.
| 8) Max. Operating Speed: |  |  | 2250 rpm
| 9) Gear Ratio: |  |  | 270:1 ratio
| 10) Displaced Volume/ Revolution: |  |  | 0.037037 cf
| 11) Drive Rate, CD: |  |  | 10 cf/rev
| 12) Drive Rate, TD: |  |  | 100 cf/rev
| 13) Odometer Turnover: |  |  | 2.28 yrs.
| 14) Nominal Pipe Size: |  |  | 3 in.
| 15) Flange-to-Flange: |  |  | 6-3/4 in.
| 16) Bolts per Flange: |  |  | 4
| 17) Flange Bolt Hole Depth |  |  | 15/16 in.
| 18) Restricting Orfice (120%): |  |  | 23/32 in.
[6 empty] | Column A | Column B | Column C | Column D | Column E
Item |  | Description |  |  |  | Quantity Each (A) | New Unit Price (B) | Subtotal (A * B) | Recertified Unit Price ( C) | Subtotal (A * C)
14 | ROMET OR ROOTS 7M ROTARY METER OR EQUIVALENT |  |  |  |  | 10 |  | 0 |  | 0
| 1) Base Rate (Q.Max) : |  |  | 7000 acfh
| 2) Rangeability (+/-1%): |  |  | 67:1 ratio
| 3) Rangeability (+/- 2%): |  |  | 115:1 ratio
| 4) Start Rate: |  |  | 5.33 cfh
| 5) Stop Rate |  |  | 3.39 cfh
| 6) Flow Rate @ 0.5" W.C. Gas: |  |  | 5400 cfh
| 7) Avg. Differential, 100% Flow: |  |  | 1.6 in. w.c.
| 8) Max. Operating Speed: |  |  | 1867 rpm
| 9) Gear Ratio: |  |  | 160:1 ratio
| 10) Displaced Volume/ Revolution: |  |  | 0.0325 cf
| 11) Drive Rate, CD: |  |  | 10 cf/rev
| 12) Drive Rate, TD: |  |  | 100 cf/rev
| 13) Odometer Turnover: |  |  | 1.63 yrs.
| 14) Nominal Pipe Size: |  |  | 3 in.
| 15) Flange-to-Flange: |  |  | 9-1/2 in.
| 16) Bolts per Flange: |  |  | 4
| 17) Flange Bolt Hole Depth |  |  | 15/16 in.
| 18) Restricting Orfice (120%): |  |  | 13/16 in.
15 | ROMET OR ROOTS 11M ROTARY METER OR EQUIVALENT |  |  |  |  | 10 |  | 0 |  | 0
| 1) Base Rate (Q.Max) : |  |  | 11000 acfh
| 2) Rangeability (+/-1%): |  |  | 124:1 ratio
| 3) Rangeability (+/- 2%): |  |  | 227:1ratio
| 4) Start Rate: |  |  | 3.88 cfh
| 5) Stop Rate |  |  | 3.23 cfh
| 6) Flow Rate @ 0.5" W.C. Gas: |  |  | 7300 cfh
| 7) Avg. Differential, 100% Flow: |  |  | 1.6 in. w.c.
| 8) Max. Operating Speed: |  |  | 1833 rpm
| 9) Gear Ratio: |  |  | 100:1 ratio
| 10) Displaced Volume/ Revolution: |  |  | 0.1 cf
| 11) Drive Rate, CD: |  |  | 10 cf/rev
| 12) Drive Rate, TD: |  |  | 100 cf/rev
| 13) Odometer Turnover: |  |  | 1.04 yrs.
| 14) Nominal Pipe Size: |  |  | 4 in.
| 15) Flange-to-Flange: |  |  | 9-1/2 in.
| 16) Bolts per Flange: |  |  | 8
| 17) Flange Bolt Hole Depth |  |  | 1-1/16 in.
| 18) Restricting Orfice (120%): |  |  | 1 in.
[6 empty] | Column A | Column B | Column C | Column D | Column E
Item |  | Description |  |  |  | Quantity Each (A) | New Unit Price (B) | Subtotal (A * B) | Recertified Unit Price ( C) | Subtotal (A * C)
16 | HSR 3/4" ANGLE BODY |  |  |  |  | 1500 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG
2) OUTLET PRESSURE: 7" W.C. TO 2LB W.C.
3) ORIFICE SIZE: 1/8"
4) VENT POSITION: SENSUS - #14; FISHER - E; ACTARIS - #13; LANCASTER - 9-9;
AMERICAN - VALVE HEAD (A) VENT #1
17 | HSR 3/4" ANGLE BODY |  |  |  |  | 500 |  | 0 |  | 0
1) INLET PRESSURE: 6 PSIG
2) OUTLET PRESSURE: 7" W.C. TO 2LB W.C.
3) ORIFICE SIZE: 3/8"
4) VENT POSITION: SENSUS - #14; FISHER - E; ACTARIS - #13; LANCASTER - 9-9;
AMERICAN - VALVE HEAD (A) VENT #1
18 | HSR 3/4" GLOBE BODY |  |  |  |  | 200 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG
2) OUTLET PRESSURE: 7" W.C. TO 2LB W.C.
3) ORIFICE SIZE: 1/8"
4) VENT POSITION: SENSUS - #14; FISHER - E; ACTARIS - #13; LANCASTER - 9-9;
AMERICAN - VALVE HEAD (A) VENT #1
19 | HSR 3/4" GLOBE BODY |  |  |  |  | 200 |  | 0 |  | 0
1) INLET PRESSURE: 6 PSIG
2) OUTLET PRESSURE: 7" W.C. TO 2LB W.C.
3) ORIFICE SIZE: 3/8"
4) VENT POSITION: SENSUS - #14; FISHER - E; ACTARIS - #13; LANCASTER - 9-9;
AMERICAN - VALVE HEAD (A) VENT #1
20 | HSR 1" GLOBE BODY |  |  |  |  | 300 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG
2) OUTLET PRESSURE: 7" W.C. TO 2LB W.C.
3) ORIFICE SIZE: 1/8"
4) VENT POSITION: SENSUS - 105; FISHER - 3F; ACTARIS - #5; LANCASTER - 6-6;
AMERICAN - VALVE HEAD (C) VENT #2
21 | HSR 1" GLOBE BODY |  |  |  |  | 300 |  | 0 |  | 0
1) INLET PRESSURE: 6 PSIG
2) OUTLET PRESSURE: 7" W.C. TO 2LB W.C.
3) ORIFICE SIZE: 3/8"
4) VENT POSITION: SENSUS - 105; FISHER - 3F; ACTARIS - #5; LANCASTER - 6-6;
AMERICAN - VALVE HEAD C VENT #2
22 | DIRECT OPERATED PRESSURE REDUCING REGULATOR |  |  |  |  | 15 |  | 0 |  | 0
1) LARGE RESIDENTIAL 10 LB OR HIGHER
2) INLET PRESSURE: 60 PSIG
3) OUTLET PRESSURE: 5-20 PSIG
4) ORIFICE SIZE: 1/4"
5) 1" BODY
6) INTERNAL RELIEF WITHOPEN THROAT
| CAPACITY | FULL RELIEF
60# INLET
10# OUT
| 1/4"ORIFICE |  | 4710SCFH
[6 empty] | Column A | Column B | Column C | Column D | Column E
Item |  | Description |  |  |  | Quantity Each (A) | New Unit Price (B) | Subtotal (A * B) | Recertified Unit Price ( C) | Subtotal (A * C)
23 | CONSTANT PRESSURE PILOT LOADED REGULATOR LT GREEN MAIN SPRING, BLUE PILOT SRING |  |  |  |  | 25 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG
2) OUTLET PRESSURE: 1LB-20LB
3) ORIFICE SIZE: 3/8" with ability to interchange
4) 2" BODY
5)INTERNAL BLEED TO PREVENT VAPOR-LOCK UP
6) VENT POSITION: SENSUS - 105; FISHER - 3F; ACTARIS - #5; LANCASTER - 6-6;
AMERICAN - VALVE HEAD C VENT #2
| CAPACITY | TOKEN RELIEF
| 60# INLET | 1-20#OUTLET
| 1/4" ORIFICE | 3/8"ORIFICE
| 4600 SCFH | 7500SCFH
24 | 2" FLANGED SPRING LOADED, SELF REGULATED GAS REGULATOR WITH INTERNAL RELIEF VALVE |  |  |  |  | 30 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG .60 SG NATURAL GAS
2) OUTLET PRESSURE: 7" W.C. TO 14" W.C.
(MUST BE CAPABLE OF OUTLET PRESSURE UP TO 2 PSI WITH ONLY A CHANGE OF SPRING)
3) BRASS ORIFICE SIZE: 3/8", WITH THE ABILITY TO INTERCHANGE ORFICES
5) ADJUSTABLE LOADING RING
| 6) 1 IN. INTERNAL RELIEF VALVE |  |  | FULL RELIEF
7) CONTROLLED SIZE BREATHER ORFICE
8) VENT POSITION: SENSUS -105; FISHER - 3F; ACTARIS - #5; LANCASTER - 6-6;
CAPACITY:
| 60# IN | 60# IN | 5#IN | 5#IN
| 7"OUT | 2# OUT | 7"OUT | 2# OUT
| 1/4"ORIFICE | 1/4"ORIFICE | 3/8 X 1/2ORIFICE | 3/8 X 1/2ORIFICE
| 4500SCFH | 4000SCFH | 2400SCFH | 1500SCFH
25 | 2" FEMALE PIPE THREAD SPRING LOADED, SELF OPERATED GAS REGULATOR WITH INTERNAL RELIEF VALVE |  |  |  |  | 30 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG .60 SG NATURAL GAS
2) OUTLET PRESSURE: 7" W.C. TO 14" W.C.
(MUST BE CAPABLE OF OUTLET PRESSURE UP TO 2 PSI WITH ONLY A CHANGE OF SPRING)
3) BRASS ORIFICE SIZE: 3/8", WITH THE ABILITY TO INTERCHANGE ORFICES
5) ADJUSTABLE LOADING RING
| 6) 1 IN. INTERNAL RELIEF VALVE |  |  | FULL RELIEF
7) CONTROLLED SIZE BREATHER ORFICE
8) VENT POSITION: SENSUS -105; FISHER - 3F; ACTARIS - #5; LANCASTER - 6-6;
CAPACITY:
| 60# IN | 60# IN | 5#IN | 5#IN
| 7"OUT | 2# OUT | 7"OUT | 2# OUT
| 1/4"ORIFICE | 1/4"ORIFICE | 3/8 X 1/2ORIFICE | 3/8 X 1/2ORIFICE
| 4500SCFH | 4000SCFH | 2400SCFH | 1500SCFH
[6 empty] | Column A | Column B | Column C | Column D | Column E
Item |  | Description |  |  |  | Quantity Each (A) | New Unit Price (B) | Subtotal (A * B) | Recertified Unit Price ( C) | Subtotal (A * C)
26 | 1 1/4" SPRING LOADED, SELF OPERATED GAS REGULATOR WITH INTERNAL RELIEF |  |  |  |  | 10 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG .60 SG NATURAL GAS
2) OUTLET PRESSURE: 7" W.C. TO 14" W.C.
(MUST BE CAPABLE OF OUTLET PRESSURE UP TO 2 PSI WITH ONLY A CHANGE OF SPRING)
3) BRASS ORIFICE SIZE: 3/8" X 1/2" with the ability to interchange orifice
5) ADJUSTABLE LOADING RING
| 6) 1 IN. INTERNAL RELIEF VALVE |  |  | FULL RELIEF
7) CONTROLLED SIZE BREATHER ORFICE
8) VENT POSITION: SENSUS -105; FISHER - 3F; ACTARIS - #5; LANCASTER - 6-6;
CAPACITY:
| 60# IN | 60# IN | 5#IN | 5#IN
| 7"OUT | 2# OUT | 7"OUT | 2# OUT
| 1/4" x 3/8" ORIFICE | 3/8 X 1/2ORIFICE | 3/8 X 1/2ORIFICE | 7/8" X 1"ORIFICE
| 4080SCFH | 3550SCFH | 1960SCFH | 1170SCFH
27 | 1 1/4" SPRING LOADED, SELF OPERATED GAS REGULATOR WITH INTERNAL RELIEF |  |  |  |  | 10 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG .60 SG NATURAL GAS
2) OUTLET PRESSURE: 7" W.C. TO 14" W.C.
(MUST BE CAPABLE OF OUTLET PRESSURE UP TO 2 PSI WITH ONLY A CHANGE OF SPRING)
3) BRASS ORIFICE SIZE: 7/8" X 1"
5) ADJUSTABLE LOADING RING
| 6) 1 IN. INTERNAL RELIEF VALVE |  |  | FULL RELIEF
7) CONTROLLED SIZE BREATHER ORFICE
8) VENT POSITION: SENSUS -105; FISHER - 3F; ACTARIS - #5; LANCASTER - 6-6;
CAPACITY:
| 60# IN | 60# IN | 5#IN | 5#IN
| 7"OUT | 2# OUT | 7"OUT | 2# OUT
| 1/4" x 3/8" ORIFICE | 3/8 X 1/2ORIFICE | 3/8 X 1/2ORIFICE | 7/8" X 1"ORIFICE
| 4080SCFH | 3550SCFH | 1960SCFH | 1170SCFH
28 | SPRING LOADED THROTTLING RELIEF BACK PRESSURE REGULATOR (OVERPRESSURE RELIEF REGULATOR) |  |  |  |  | 25 |  | 0 |  | 0
1) 1 INCH BODY
2) 15#-50# INTEGRAL
29 | SPRING LOADED THROTTLING RELIEF BACK PRESSURE REGULATOR (OVERPRESSURE RELIEF REGULATOR) |  |  |  |  | 25 |  | 0 |  | 0
1) 1 INCH BODY
2) 4LB-15LB INTEGRAL
30 | PILOT OPERATED PRESSURE REDUCING REGULATOR |  |  |  |  | 5 |  | 0 |  | 0
Distribution, Industrial, and Commercial applications
1) Inlet: Up to 175 psig/12.1 bar
2) Outlet: 1-20# (Large commercial and reg, stations)
3) Integral Token Relief (designed to relieve overpressure caused by thermal expansion
4) Orifice: 1/2"
[6 empty] | Column A | Column B | Column C | Column D | Column E
Item |  | Description |  |  |  | Quantity Each (A) | New Unit Price (B) | Subtotal (A * B) | Recertified Unit Price ( C) | Subtotal (A * C)
31 | PRESSURE REDUCING REGULATOR FOR REGULATOR STATIONS AND DISTRIC GATE STATIONS |  |  |  |  | 5 |  | 0 |  | 0
1) Inlet: Up to 1000 psig/69.1 bar
2) Outlet: 2" W.C.to 100 psig
3)Brass Seat
4)Orifice: 7/8"
5) Internal pressure registration
6) 2 inch flanged body
32 | STRAINERS |  |  |  |  | 50 |  | 0 |  | 0
1) 2" Threaded body
2) 100 mesh
33 | FILTER 2" (DRY PARTICLE) |  |  |  |  | 10 |  | 0 |  | 0
1) 2" Flanged body
2) 180 psig max
3) 10 micron filter
34 | FILTER 3" (DRY PARTICLE) |  |  |  |  | 2 |  | 0 |  | 0
1) 3" Flanged body
2) 180 psig max
3) 10 micron filter
35 | FILTER 4" (DRY PARTICLE) |  |  |  |  | 2 |  | 0 |  | 0
1) 4" Flanged body
2) 180 psig max
3) 10 micron filter
[5 empty] | GRAND TOTALS: |  | Total for New Units (Total of Column C) |  | Total for Recertified Units (Total of Column E)
[7 empty] | 0 |  | 0