## Sheet1
Clearwater Preferred Product List
The list of preferred products shall be used for the construction of water and reclaimed water utilities for the City of Clearwater. This list does not relieve the Contractor from their responsiblity to conform to the City's Technical Specifications and Construction Standard Details. Products submitted for use on City projects which are not included in the list below shall be subject to the review and approval by the City.
Cat. | Description | Manufacturer | Potable Water |  | Reclaimed Water |  | Change/Alteration
|  |  | Model | Comments | Model | Comments
Air Release Valve | ARV Enclosure | Water Plus Polyethelene Enclosure | H-20 | Blue 28" Tall | H-20 | Pantone 28" Tall | Previous City detail only included 28" Size. Additional sizes added to accommodate other potential ARV Models.
|  |  | H-30 | Blue 44" Tall | H-30 | Pantone 44" Tall
|  |  | H-40 | Blue 30" Tall | H-40 | Pantone 30" Tall
|  | DFW Plastics |  | Blue |  | Purple
| Air Release Valve | ARI | D-040 SS or Nylon | Combination | D-041SS | Combination | H-TEC Previously specified. Additional models added. ARI model per manufacturer recommendation and listed as an approved product for Pinellas County and Orange County. Vent-o-Mat model per manufacturer recommendation and listed as an approved product for Orange County
|  | H-TEC | SS 993 |  | SS993
|  | Vent-o-Mat | Series RBX DN50 |  | Series RBX DN50
Casing Seals/Spacers | Casing Seals | Advance Products | Model AC and AW |  | Model AC and AW |  | Originally provided specifications only included Cascade as a manufactuer. The additional manufactuers added provide additional options. Added manufacturers are also included for Pinellas County, Hillsborough County, and Orange County
|  | BWM Company | Model WR and PO |  | Model WR and PO
|  | Cascade Water Works | Model CCES |  | Model CCES
|  | CCI Pipeline | Model ESW and ESC |  | Model ESW and ESC
|  | Pipeline Seal & Insulator | Model C and W |  | Model C and W
|  | Power Seal | Model 4810ES |  | Model 4810ES
| Casing Spacer | Advance Products | SS18/SS112 |  | SS18/SS112
|  | BWM Company | BWM-SS8/SS-12 |  | BWM-SS8/SS-12
|  | Cascade Water Works | Series CCS |  | Series CCS
|  | CCI Pipeline | Model CCS8 |  | Model CCS8
|  | Pipeline Seal & Insulator | Series S8G/S12G-2 |  | Series S8G/S12G-2
Coatings | Exterior Coating for Exposed Metal Assets | Zinc/ Urethane/ Fluoropolymer system for above ground piping |  |  |  |  | Coatings not previously specified in the original specifications and no previous manufacturer specified. The provided coatings are based on manufacturer recommendations.
|  | Carboline | Primer: Carbozinc 621 | 3.0-8.0 mils | Primer: Carbozinc 621 | 3.0-8.0 mils
|  |  | 1st Coat: Carbothane 133 HB | 3.0-5.0 mils | 1st Coat: Carbothane 133 HB | 3.0-5.0 mils
|  |  | 2nd Coat: Carboxane 950 | 2.0-3.0 mils | 2nd Coat: Carboxane 950 | 2.0-3.0 mils
|  | Tnemec | Primer: Series 90-97 Tnemec-Zinc | 2.5-3.5 mils | Primer: Series 90-97 Tnemec-Zinc | 2.5-3.5 mils
|  |  | 1st Coat: Series 66 Hi-Build Epoxoline | 2.0-6.0 mils | 1st Coat: Series 66 Hi-Build Epoxoline | 2.0-6.0 mils
|  |  | 2nd Coat: Series 700 Hydroflon | 2.0-3.0 mils | 2nd Coat: Series 700 Hydroflon | 2.0-3.0 mils
Zinc/Epoxy/Urethane system for above ground piping
|  | Carboline | Carbozinc 621 | 3.0-8.0 mils | Carbozinc 621 | 3.0-8.0 mils
|  |  | Carboguard 60 | 4.0-6.0 mils | Carboguard 60 | 4.0-6.0 mils
|  |  | Carboxane 950 | 2.0-3.0 mils | Carboxane 950 | 2.0-3.0 mils
|  | Tnemec | Series 90-97 Tnemec-Zinc | 2.5-3.5 mils | Series 90-97 Tnemec-Zinc | 2.5-3.5 mils
|  |  | Series 66 Hi-Build Epoxoline | 2.0-6.0 mils | Series 66 Hi-Build Epoxoline | 2.0-6.0 mils
|  |  | Series 1095 Urethane | 4.0-10.0 mils | Series 1095 Urethane | 4.0-10.0 mils
Polyamide Epoxy- Coal Tar for Burried Pipes
|  | Tnemec | 1st Coat: Series 46H-413 Hi-Build Tneme Tar | 8-10.0 Mils | 1st Coat: Series 46H-413 Hi-Build Tneme Tar | 8-10.0 Mils
|  |  | 2nd Coat: Series 46H-413 Hi-Build Tneme Tar | 8-10.0 Mils | 2nd Coat: Series 46H-413 Hi-Build Tneme Tar | 8-10.0 Mils
Fittings | Ductile Iron Fittings | American |  | Cement or FBE Lined |  | Cement or FBE Lined | No previous manufacturer specified. Provided list of manufacturers meets original and updated specifications. Listed manufacturers are found on approved product lists for Pinellas County, Hillsborough County, and Orange County
|  | Sigma |  | Cement or FBE Lined |  | Cement or FBE Lined
|  | Star |  | Cement or FBE Lined |  | Cement or FBE Lined
|  | Tyler Union |  | Cement or FBE Lined |  | Cement or FBE Lined
Hydrants | Hydrants | American Flow Control | Darling B-84-B-5 |  | Hydrants are not acceptable for Reclaimed Water Applicatons. |  | No Change.
|  | AVK | Nostalgic 2780
|  | EJ Co. | Watermaster 5CD250
|  | Kennedy | Guardian No. K-81D
|  | Mueller | Super Centurion No 250
Joint Restraints | Ductile Iron Pipe MJ Restraint | EBAA Iron | Megalug Series 1100 |  | Megalug Series 1100 |  | Restraints for ductile iron pipe and fittings were not specifically specified in the original standard specifications and no previous manufacturers were specified. Listed manufacturers are found on approved product lists for Pinellas County, Hillsborough County, and Orange County
|  | Ford/Uniflange | UFR-1400 |  | UFR-1400
|  | Sigma | OneLok Series SLD/SLDE |  | OneLok Series SLD/SLDE
|  | Smith Blair | Camlock Series 111 |  | Camlock Series 111
|  | Star | Star Grip Series 3000 |  | Star Grip Series 3000
|  | Tyler Union | TufGrip Series TLD |  | TufGrip Series TLD
| Ductile Iron Pipe Bell Joint Restraints (4-12") | EBAA Iron | Tru-Dual Series 1500 TD |  | Tru-Dual Series 1500 TD
|  | Ford/Uniflange | Uni-Flange Series 1390C |  | Uni-Flange Series 1390C
|  | Sigma | PV-Lok Series PWP-C |  | PV-Lok Series PWP-C
|  | Smith Blair | Bell-Lock Series 165 |  | Bell-Lock Series 165
|  | Star | StarGrip Series 3100S |  | StarGrip Series 3100S
|  | Tyler Union | TufGrip-Series 300C |  | TufGrip-Series 300C
| Ductile Iron Pipe Bell Joint Restraints (>16") | EBAA Iron | Series 1100HD |  | Series 1100HD
|  | Sigma | Series SSLDH |  | Series SSLDH
|  | Star | Series 3100S |  | Series 3100S
| Ductile Iron Pipe Joint Restraint Gaskets and Locking Bell | American | Fast Grip Gasket | Gasket | Fast Grip Gasket | Gasket
|  |  | Flex Ring Joint | Bell Lock | Flex Ring Joint | Bell Lock
|  |  | Lok Ring Joint | Bell Lock | Lok Ring Joint | Bell Lock
|  | McWane | Sure Stop 350 Gasket | Gasket | Sure Stop 350 Gasket | Gasket
|  |  | Thrust Lock | Bell Lock | Thrust Lock | Bell Lock
|  |  | TR- Flex | Bell Lock | TR- Flex | Bell Lock
|  | US Pipe | Field Lok 350 Gasket | Gasket | Field Lok 350 Gasket | Gasket
|  |  | Field Lok Gasket | Gasket | Field Lok Gasket | Gasket
|  |  | TR-Flex | Bell Lock | TR-Flex | Bell Lock
|  |  | HP Lok Restraint Joint | Bell Lock | HP Lok Restraint Joint | Bell Lock
| PVC Pipe MJ Restraint | EBAA Iron | Megalug Series 2000PV |  | Megalug Series 2000PV |  | Previous City specification provided Megalug by EBAA Iron Series 2000 PV or approved equal. Additoinal manufacturers listed as apprroved equal options and are also listed in approved product lists for Pinellas County, Hillsborough County, and Orange County
|  | Ford/Uniflange | UFR 1500 Series |  | UFR 1500 Series
|  | Sigma | One Lok Series SLC/SLE |  | One Lok Series SLC/SLE
|  | Smith Blair | Cam Lok Series 120 |  | Cam Lok Series 120
|  | Star | Star Grip Series 4000 |  | Star Grip Series 4000
|  | Tyler Union | TufGrip Series TLP |  | TufGrip Series TLP
| PVC Bell Joint Restraint (4"-12") (New and Existing) | EBAA Iron | Series 1600 |  | Series 1600 |  | Previous City specification provided Megalug by EBAA Iron Series 1600 or approved equal. Additoinal manufacturers listed as apprroved equal options and are also listed in approved product lists for Pinellas County, Hillsborough County, and Orange County
|  | Ford/Uniflange | Uni-Flange Series 1390 |  | Uni-Flange Series 1390
|  | Sigma | PV-Lok Series PWP |  | PV-Lok Series PWP
|  | Smith Blair | Bell-Lock Series 165 |  | Bell-Lock Series 165
|  | Star | Series 1100C |  | Series 1100C
|  | Tyler Union | TufGrip 300C |  | TufGrip 300C
Locator Wire | Locator Wire | Copperhead Industries | 1045B-EHS | Open Cut or Directional Drill | 1045P-EHS | Open Cut or Directional Drill | Previous City specification provided Copperhead Industries Only as an approved manufactuerer. However, the approved model provided improves from 12 gauge to 10 gauge wire. Additonally, a different wire model is added for heavier duty applications as necessary.
|  |  | 3/16B-PB | Pipe Bursting | 3/16P-PB | Pipe Bursting
|  | Protrace | HDD-CCS PE45 | Open Cut or Directional Drill | HDD-CCS PE45 | Open Cut or Directional Drill
|  | Agave | BT-1001 | Open Cut or Directional Drill | BT-1001 | Open Cut or Directional Drill
|  |  | BT-3/16SS | Pipe Bursting | BT-3/16SS | Pipe Bursting
Pipe | PVC C900 DR 18 Bell and Spigot (Up to 12") | Diamond Plastics Corp | C-900 | Blue | C-900 | Pantone Purple | No previous manufacturer specified. Provided list of manufacturers meets original and updated specifications. Listed manufacturers are found on approved product lists for Pinellas County, Hillsborough County, and Orange County.
|  | JM Eagle | C-900 | Blue | C-900 | Pantone Purple
|  | National Pipe & Plastics | C-900 | Blue | C-900 | Pantone Purple
|  | North American Pipe Corp | C-900 | Blue | C-900 | Pantone Purple
| Restrained Joint PVC Pipe for Directional Drilling | CertainTeed | Certa-Lok-C900 |  | Certa-Lok-C900 |  | No changes from originally specified manufacturer.
|  | JM Eagle | Eagle Loc 900 |  | Eagle Loc 900
| HDPE C906 DR 11 | JM Eagle |  | DR-11 Blue |  | DR-11 Pantone Purple | No previous manufacturer specified. Provided list of manufacturers meets original and updated specifications. Listed manufacturers are found on approved product lists for Pinellas County, Hillsborough County, and Orange County.
|  | Performance Pipe (Chevron) |  | DR-11 Blue |  | DR-11 Pantone Purple
|  | Poly Pipe |  | DR-11 Blue |  | DR-11 Pantone Purple
| Ductile Iron Pipe | American | Cement Lined |  | Cement Lined
|  | Griffin | Cement Lined |  | Cement Lined
|  | McWane | Cement Lined |  | Cement Lined
|  | US Pipe | Cement Lined |  | Cement Lined
Polywrap | Polywrap | American |  | Blue |  | Pantone Purple | Polywrap was not previously specificed in the standardized specifications and no previous manufacturer specified. Listed manufacturers are found on approved product lists for Pinellas County, Hillsborough County, and Orange County
|  | Christys |  | Blue |  | Pantone Purple
|  | Trumbull |  | Blue |  | Pantone Purple
|  | US Pipe |  | Blue |  | Pantone Purple
Repair Clamp | Repair Clamp | JCM | JCM 118 |  | JCM 118 |  | Repair Clamp was not previously included in the City's standard specifications.
|  | Romac | SS2 or SS3 |  | SS2 or SS3
Services | Ductile Iron Service Saddle | Ford | FC202 |  | FC202 |  | Existing detail lists only Ford FC202 or equal. Additional products listed are equal and also included on approved product lists for Pinellas County, Hillsborough County, and Orange County
|  | JCM | Series 406 |  | Series 406
|  | Mueller | DR2S Series |  | DR2S Series
|  | Romac | 202N Series |  | 202N Series
|  | Smith Blair | 397, 317 Series |  | 397, 317 Series
| Service Saddle for HDPE Pipe | Ford | FCP-202 Series | With Spring Washers | FCP-202 Series | With Spring Washers | No service saddles for HDPE pipe previously included. Products listed are included on the approved product lists for Pinellas County, Hillsborough County, and Orange County.
|  | JCM | Series 406 | With Spring Washers | Series 406 | With Spring Washers
|  | Romac | 202N-H Series | With Spring Washers | 202N-H Series | With Spring Washers
|  | Smith Blair | 317 Series | With Spring Washers | 317 Series | With Spring Washers
| Corporation Stop- Threaded | Ford | FB400-6 | 1 1/2" | FBRW1000-4Q | 1" shall be ball corporation stop. 2" shall be threaded corporation stop. | No Change, previously detailed in City Standard Details
|  |  | FB400-7 | 2"
|  | Mueller | H-10003N | 1" | B-25008-20
|  |  | B-2996N | 1 1/2"
|  |  | B-2996N | 2"
| Curb Stops | Ford | B43-332 WQ | with Lock Wing and Compression Inlet | BRW 43-444W-Q | Reclaimed Water shall be stamped on curb stops | No Change, previously detailed in City Standard Details
BRW 41-777W-Q
|  | Mueller | Mueller H24350 | with Lock Wing and Compression Inlet | B24353 N-20
B25170 N-20
| Polyethylene Tubing | Charter |  |  |  |  | No manufacturers previously listed in original specifications. Provided list of manufacturers meets original and updated specifications. Manufacturers listed are included on Approved Product Lists for Pinellas County, Hillsborough County, and Orange County
Endot
JM Eagle
| Meter Boxes | Armorcast Product |  |  |  |  | No manufacturers previously listed. Provided list of manufacturers meets original and updated specifications. Manufactures listed are included on Approved Product Lists for Pinellas County, Hillsborough County, and Orange County
Carson
Hubbell
Tapping Sleeves and Valves | Line Stops | JCM | JCM 442 |  | JCM 442 |  | No linestops previously included. Rangeline has confirmed that these linestops are acceptable. EA Tapping has yet to return response
|  | Smith Blair | 680 |  | 680
| Tapping Sleeves | JCM | JCM 412 |  | JCM 412 |  | Original City specification identified JCM 412 or Smith Blair 662 as acceptable options. JCM 452 added as a stainless steel option as necessary.
|  |  | JCM 452 |  | JCM 452
|  | Smith Blair | 622 |  | 622
| Tapping Valve | American | Seriess 2500 |  | Seriess 2500 |  | No previous manufacturer specified. Listed manufacturers are found on approved product lists for Pinellas County, Hillsborough County, and Orange County
|  | Clow | Series F-6114 |  | Series F-6114
|  | Mueller | Series T2361 |  | Series T2361
Valves | Butterfly Valve | Clow | #1450 | 24" and above | #1450 | 24" and above | No previous manufacturer specified. Provided list of manufacturers meets original and updated specifications. Listed manufacturers are found on approved product lists for Pinellas County, Hillsborough County, and Orange County
|  | Dezurik | BAW | 24" and above | BAW | 24" and above
|  | Pratt |  | 24" and above |  | 24" and above
| Gate Valve | American | Series 2500 NRS |  | Series 2500 NRS
|  | Clow | Series F-6100 |  | Series F-6100
|  | Mueller | Series A-2360 |  | Series A-2360
| OS&Y Valves | American | Series 2500 OS&Y |  | Series 2500 OS&Y
|  | Clow | 2638, 2639, or 2640 |  | 2638, 2639, or 2640
|  | Mueller | R-2360 |  | R-2360
Valve Box | Sigma | [5 empty] | No previous manufacturer specified. Listed manufacturers are found on approved product lists for Pinellas County, Hillsborough County, and Orange County
Star
Tyler Union