## EXHIBIT A
[7 empty] | Column A | Column B | Column C | Column D | Column E
Item |  | Description |  |  | Manufacturer | Part/ Item Number | Quantity Each (A) | New Unit Price (B) | Subtotal (A * B) | Recertified Unit Price ( C) | Subtotal (A * C)
1 | HSR 3/4" ANGLE BODY | [5 empty] | 1500 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG
2) OUTLET PRESSURE: 7" W.C. TO 2LB W.C.
3) ORIFICE SIZE: 1/8"
4) VENT POSITION: SENSUS - #14; FISHER - E; ACTARIS - #13; LANCASTER - 9-9;
AMERICAN - VALVE HEAD (A) VENT #1
2 | HSR 3/4" ANGLE BODY | [5 empty] | 500 |  | 0 |  | 0
1) INLET PRESSURE: 6 PSIG
2) OUTLET PRESSURE: 7" W.C. TO 2LB W.C.
3) ORIFICE SIZE: 3/8"
4) VENT POSITION: SENSUS - #14; FISHER - E; ACTARIS - #13; LANCASTER - 9-9;
AMERICAN - VALVE HEAD (A) VENT #1
3 | HSR 3/4" GLOBE BODY | [5 empty] | 200 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG
2) OUTLET PRESSURE: 7" W.C. TO 2LB W.C.
3) ORIFICE SIZE: 1/8"
4) VENT POSITION: SENSUS - #14; FISHER - E; ACTARIS - #13; LANCASTER - 9-9;
AMERICAN - VALVE HEAD (A) VENT #1
4 | HSR 3/4" GLOBE BODY | [5 empty] | 200 |  | 0 |  | 0
1) INLET PRESSURE: 6 PSIG
2) OUTLET PRESSURE: 7" W.C. TO 2LB W.C.
3) ORIFICE SIZE: 3/8"
4) VENT POSITION: SENSUS - #14; FISHER - E; ACTARIS - #13; LANCASTER - 9-9;
AMERICAN - VALVE HEAD (A) VENT #1
5 | HSR 1" GLOBE BODY | [5 empty] | 300 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG
2) OUTLET PRESSURE: 7" W.C. TO 2LB W.C.
3) ORIFICE SIZE: 1/8"
4) VENT POSITION: SENSUS - 105; FISHER - 3F; ACTARIS - #5; LANCASTER - 6-6;
AMERICAN - VALVE HEAD (C) VENT #2
6 | HSR 1" GLOBE BODY | [5 empty] | 300 |  | 0 |  | 0
1) INLET PRESSURE: 6 PSIG
2) OUTLET PRESSURE: 7" W.C. TO 2LB W.C.
3) ORIFICE SIZE: 3/8"
4) VENT POSITION: SENSUS - 105; FISHER - 3F; ACTARIS - #5; LANCASTER - 6-6;
AMERICAN - VALVE HEAD C VENT #2
7 | DIRECT OPERATED PRESSURE REDUCING REGULATOR (Equivalent to Fisher 627) | [5 empty] | 15 |  | 0 |  | 0
1) LARGE RESIDENTIAL 10 LB OR HIGHER
2) INLET PRESSURE: 60 PSIG
3) OUTLET PRESSURE: 5-20 PSIG
4) ORIFICE SIZE: 1/4"
5) 1" BODY
6) INTERNAL RELIEF WITHOPEN THROAT
| CAPACITY | FULL RELIEF
60# INLET
10# OUT
| 1/4"ORIFICE |  | 4710SCFH
[7 empty] | Column A | Column B | Column C | Column D | Column E
Item |  | Description |  |  | Manufacturer |  | Quantity Each (A) | New Unit Price (B) | Subtotal (A * B) | Recertified Unit Price ( C) | Subtotal (A * C)
8 | CONSTANT PRESSURE PILOT LOADED REGULATOR LT GREEN MAIN SPRING, BLUE PILOT SRING (Equivalent to Itron CL231) | [5 empty] | 25 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG
2) OUTLET PRESSURE: 1LB-20LB
3) ORIFICE SIZE: 3/8" with ability to interchange
4) 2" BODY
5)INTERNAL BLEED TO PREVENT VAPOR-LOCK UP
6) VENT POSITION: SENSUS - 105; FISHER - 3F; ACTARIS - #5; LANCASTER - 6-6;
AMERICAN - VALVE HEAD C VENT #2
| CAPACITY | TOKEN RELIEF
| 60# INLET | 1-20#OUTLET
| 1/4" ORIFICE | 3/8"ORIFICE
| 4600 SCFH | 7500SCFH
9 | 2" FLANGED SPRING LOADED, SELF REGULATED GAS REGULATOR WITH INTERNAL RELIEF VALVE (Equivalent to Itron B34) | [5 empty] | 30 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG .60 SG NATURAL GAS
2) OUTLET PRESSURE: 7" W.C. TO 14" W.C.
(MUST BE CAPABLE OF OUTLET PRESSURE UP TO 2 PSI WITH ONLY A CHANGE OF SPRING)
3) BRASS ORIFICE SIZE: 3/8", WITH THE ABILITY TO INTERCHANGE ORFICES
4) 10" BODY (FLANGE LENGTH)
5) ADJUSTABLE LOADING RING
| 6) 1 IN. INTERNAL RELIEF VALVE |  |  | FULL RELIEF
7) CONTROLLED SIZE BREATHER ORFICE
8) VENT POSITION: SENSUS -105; FISHER - 3F; ACTARIS - #5; LANCASTER - 6-6;
CAPACITY:
| 60# IN | 60# IN | 5#IN | 5#IN
| 7"OUT | 2# OUT | 7"OUT | 2# OUT
| 1/4"ORIFICE | 1/4"ORIFICE | 3/8 X 1/2ORIFICE | 3/8 X 1/2ORIFICE
| 4500SCFH | 4000SCFH | 2400SCFH | 1500SCFH
10 | 2" FEMALE PIPE THREAD SPRING LOADED, SELF OPERATED GAS REGULATOR WITH INTERNAL RELIEF VALVE (Equivalent to Itron B34) | [5 empty] | 30 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG .60 SG NATURAL GAS
2) OUTLET PRESSURE: 7" W.C. TO 14" W.C.
(MUST BE CAPABLE OF OUTLET PRESSURE UP TO 2 PSI WITH ONLY A CHANGE OF SPRING)
3) BRASS ORIFICE SIZE: 3/8", WITH THE ABILITY TO INTERCHANGE ORFICES
5) ADJUSTABLE LOADING RING
| 6) 1 IN. INTERNAL RELIEF VALVE |  |  | FULL RELIEF
7) CONTROLLED SIZE BREATHER ORFICE
8) VENT POSITION: SENSUS -105; FISHER - 3F; ACTARIS - #5; LANCASTER - 6-6;
CAPACITY:
| 60# IN | 60# IN | 5#IN | 5#IN
| 7"OUT | 2# OUT | 7"OUT | 2# OUT
| 1/4"ORIFICE | 1/4"ORIFICE | 3/8 X 1/2ORIFICE | 3/8 X 1/2ORIFICE
| 4500SCFH | 4000SCFH | 2400SCFH | 1500SCFH
[7 empty] | Column A | Column B | Column C | Column D | Column E
Item |  | Description |  |  | Manufacturer |  | Quantity Each (A) | New Unit Price (B) | Subtotal (A * B) | Recertified Unit Price ( C) | Subtotal (A * C)
11 | 1 1/4" SPRING LOADED, SELF OPERATED GAS REGULATOR WITH INTERNAL RELIEF (Equivalent to Itron B34SR) | [5 empty] | 10 |  | 0 |  | 0
1) INLET PRESSURE: 60 PSIG .60 SG NATURAL GAS
2) OUTLET PRESSURE: 7" W.C. TO 14" W.C.
(MUST BE CAPABLE OF OUTLET PRESSURE UP TO 2 PSI WITH ONLY A CHANGE OF SPRING)
3) BRASS ORIFICE SIZE: 7/8" X 1"
5) ADJUSTABLE LOADING RING
| 6) 1 IN. INTERNAL RELIEF VALVE |  |  | FULL RELIEF
7) CONTROLLED SIZE BREATHER ORFICE
8) VENT POSITION: SENSUS -105; FISHER - 3F; ACTARIS - #5; LANCASTER - 6-6;
CAPACITY:
| 60# IN | 60# IN | 5#IN | 5#IN
| 7"OUT | 2# OUT | 7"OUT | 2# OUT
| 1/4" x 3/8" ORIFICE | 3/8 X 1/2ORIFICE | 3/8 X 1/2ORIFICE | 7/8" X 1"ORIFICE
| 4080SCFH | 3550SCFH | 1960SCFH | 1170SCFH
12 | SPRING LOADED THROTTLING RELIEF BACK PRESSURE REGULATOR (OVERPRESSURE RELIEF REGULATOR)(Equivalent to Fisher 289) | [5 empty] | 25 |  | 0 |  | 0
1) 1 INCH BODY
2) 15#-50# INTEGRAL
13 | SPRING LOADED THROTTLING RELIEF BACK PRESSURE REGULATOR (OVERPRESSURE RELIEF REGULATOR)(Equivalent to Fisher 289) | [5 empty] | 25 |  | 0 |  | 0
1) 1 INCH BODY
2) 4LB-15LB INTEGRAL
14 | PILOT OPERATED PRESSURE REDUCING REGULATOR (Equivalent to Fisher 299) | [5 empty] | 5 |  | 0 |  | 0
Distribution, Industrial, and Commercial applications
1) Inlet: Up to 175 psig/12.1 bar
2) Outlet: 1-20# (Large commercial and reg, stations)
3) Integral Token Relief (designed to relieve overpressure caused by thermal expansion
4) Orifice: 1/2"
5) 10" Flange Length (Body Length)
15 | PRESSURE REDUCING REGULATOR FOR REGULATOR STATIONS AND DISTRIC GATE STATIONS (Equivalent to Fisher 99) | [5 empty] | 5 |  | 0 |  | 0
1) Inlet: Up to 1000 psig/69.1 bar
2) Outlet: 2" W.C.to 100 psig
3)Brass Seat
4)Orifice: 7/8"
5) Internal pressure registration
6) 2 inch flanged body
[5 empty] | GRAND TOTALS: |  |  | Total for New Units (Total of Column C) |  | Total for Recertified Units (Total of Column E)
[8 empty] | 0 |  | 0